## input
Design Parameters
Space Heating | 7 | kW
Domestic Hot Water | 23 | kW
Supply Temperature | 70 | °C
Return Temperature (SH) | 40 | °C
Return Temperature (DHW) | 12 | °C
Length (Critical Route) | 818.6006 | m
Pump Head Lift | 2 | bar
Differential Pressure (End-User) | 0.5 | bar
Maximum Pressure Gradient (Target Pressure Loss) | 183.2395 | Pa/m

## PipeList
Pipe Segment No | Predecessor Node | Successor Node | Length | Pipe Diameter | Pump Head Lift | Cumulative Number of Consumers | Has Bend | x Coordinate | y Coordinate
0 | 1 | 2 | 154 | 107.1 | 2 | 214 | 0
1 | 2 | 3 | 17.1227 | 70.3 | 0 | 47 | 0
2 | 3 | 4 | 15.5022 | 37.2 | 0 | 9 | 0
3 | 4 | 5 | 15.8944 | 37.2 | 0 | 8 | 0
4 | 5 | 6 | 17.8948 | 37.2 | 0 | 7 | 0
5 | 6 | 7 | 13.6141 | 37.2 | 0 | 6 | 0
6 | 7 | 8 | 18.2521 | 37.2 | 0 | 5 | 0
7 | 8 | 9 | 12.4017 | 26 | 0 | 4 | 0
8 | 9 | 10 | 17.8443 | 26 | 0 | 3 | 0
9 | 10 | 11 | 13.1768 | 26 | 0 | 2 | 0
10 | 11 | 12 | 18.2192 | 20 | 0 | 1 | 0
11 | 3 | 13 | 15.2383 | 54.5 | 0 | 38 | 0
12 | 13 | 14 | 20.5732 | 54.5 | 0 | 37 | 0
13 | 14 | 15 | 15.1593 | 54.5 | 0 | 36 | 0
14 | 15 | 16 | 17.8443 | 43.1 | 0 | 16 | 0
15 | 16 | 17 | 13.1768 | 43.1 | 0 | 14 | 0
16 | 17 | 18 | 18.2192 | 37.2 | 0 | 12 | 0
17 | 18 | 19 | 16.2957 | 37.2 | 0 | 10 | 0
18 | 19 | 20 | 23.2662 | 37.2 | 0 | 8 | 0
19 | 20 | 21 | 14.7271 | 37.2 | 0 | 6 | 0
20 | 21 | 22 | 21.319 | 26 | 0 | 4 | 0
21 | 22 | 23 | 15.5215 | 26 | 0 | 2 | 0
22 | 15 | 24 | 63.2604 | 43.1 | 0 | 20 | 0
23 | 24 | 25 | 11.6524 | 43.1 | 0 | 14 | 0
24 | 25 | 26 | 15.5022 | 37.2 | 0 | 13 | 0
25 | 26 | 27 | 6.2009 | 37.2 | 0 | 12 | 0
26 | 27 | 28 | 11.6524 | 37.2 | 0 | 11 | 0
27 | 28 | 29 | 16.2957 | 37.2 | 0 | 9 | 0
28 | 29 | 30 | 6.976 | 37.2 | 0 | 8 | 0
29 | 30 | 31 | 15.1196 | 37.2 | 0 | 7 | 0
30 | 31 | 32 | 12.4259 | 37.2 | 0 | 5 | 0
31 | 32 | 33 | 8.5262 | 26 | 0 | 4 | 0
32 | 33 | 34 | 9.3013 | 26 | 0 | 3 | 0
33 | 34 | 35 | 6.2009 | 26 | 0 | 2 | 0
34 | 35 | 36 | 9.7584 | 20 | 0 | 1 | 0
35 | 24 | 37 | 64.6507 | 37.2 | 0 | 6 | 1 | 1052 | 986
36 | 37 | 38 | 14.3866 | 37.2 | 0 | 5 | 0
37 | 38 | 39 | 18.3178 | 26 | 0 | 4 | 0
38 | 39 | 40 | 15.8944 | 26 | 0 | 3 | 0
39 | 40 | 41 | 18.6187 | 26 | 0 | 2 | 0
40 | 41 | 42 | 13.1768 | 20 | 0 | 1 | 0
41 | 2 | 43 | 18.6187 | 107.1 | 0 | 167 | 0
42 | 43 | 44 | 24.4436 | 37.2 | 0 | 8 | 0
43 | 44 | 45 | 13.1996 | 37.2 | 0 | 7 | 0
44 | 45 | 46 | 16.7053 | 37.2 | 0 | 6 | 0
45 | 46 | 47 | 13.1768 | 37.2 | 0 | 5 | 0
46 | 47 | 48 | 15.5215 | 26 | 0 | 4 | 0
47 | 48 | 49 | 15.5215 | 26 | 0 | 3 | 0
48 | 49 | 50 | 16.2957 | 26 | 0 | 2 | 0
49 | 50 | 51 | 13.9735 | 20 | 0 | 1 | 0
50 | 43 | 52 | 43.8365 | 107.1 | 0 | 159 | 0
51 | 52 | 53 | 18.6671 | 37.2 | 0 | 5 | 0
52 | 53 | 54 | 16.6693 | 26 | 0 | 4 | 0
53 | 54 | 55 | 10.5284 | 26 | 0 | 3 | 0
54 | 55 | 56 | 58.5322 | 26 | 0 | 2 | 0
55 | 56 | 57 | 13.6141 | 20 | 0 | 1 | 0
56 | 52 | 58 | 133.8583 | 107.1 | 0 | 154 | 0
57 | 58 | 59 | 161.7666 | 70.3 | 0 | 53 | 1 | 427 | 742
58 | 59 | 60 | 25.8531 | 37.2 | 0 | 7 | 0
59 | 60 | 61 | 17.4184 | 37.2 | 0 | 6 | 0
60 | 61 | 62 | 17.2015 | 37.2 | 0 | 5 | 0
61 | 62 | 63 | 16.1847 | 26 | 0 | 4 | 0
62 | 63 | 64 | 19.6089 | 26 | 0 | 3 | 0
63 | 64 | 65 | 19.928 | 26 | 0 | 2 | 0
64 | 65 | 66 | 19.1202 | 20 | 0 | 1 | 0
65 | 59 | 67 | 13.1996 | 70.3 | 0 | 46 | 0
66 | 67 | 68 | 13.5367 | 37.2 | 0 | 13 | 0
67 | 68 | 69 | 13.6141 | 37.2 | 0 | 12 | 0
68 | 69 | 70 | 24.4743 | 37.2 | 0 | 10 | 0
69 | 70 | 71 | 19.4396 | 37.2 | 0 | 8 | 0
70 | 71 | 72 | 15.6756 | 37.2 | 0 | 6 | 0
71 | 72 | 73 | 14.4698 | 26 | 0 | 4 | 0
72 | 73 | 74 | 16.1196 | 26 | 0 | 2 | 0
73 | 67 | 75 | 67.5946 | 54.5 | 0 | 33 | 0
74 | 75 | 76 | 9.8807 | 37.2 | 0 | 5 | 0
75 | 76 | 77 | 22.2093 | 26 | 0 | 4 | 0
76 | 77 | 78 | 22.2093 | 26 | 0 | 3 | 0
77 | 78 | 79 | 21.1563 | 26 | 0 | 2 | 0
78 | 79 | 80 | 23.9407 | 20 | 0 | 1 | 0
79 | 75 | 81 | 21.4384 | 37.2 | 0 | 9 | 0
80 | 81 | 82 | 17.6497 | 37.2 | 0 | 8 | 0
81 | 82 | 83 | 18.1531 | 37.2 | 0 | 7 | 0
82 | 83 | 84 | 18.8592 | 37.2 | 0 | 6 | 0
83 | 84 | 85 | 19.1751 | 37.2 | 0 | 5 | 0
84 | 85 | 86 | 20.0707 | 26 | 0 | 4 | 0
85 | 86 | 87 | 21.1492 | 26 | 0 | 3 | 0
86 | 87 | 88 | 16.5699 | 26 | 0 | 2 | 0
87 | 88 | 89 | 14.1444 | 20 | 0 | 1 | 0
88 | 75 | 90 | 26.744 | 43.1 | 0 | 19 | 0
89 | 90 | 91 | 21.7376 | 37.2 | 0 | 9 | 0
90 | 91 | 92 | 20.8344 | 37.2 | 0 | 8 | 0
91 | 92 | 93 | 22.1957 | 37.2 | 0 | 7 | 0
92 | 93 | 94 | 19.1751 | 37.2 | 0 | 6 | 0
93 | 94 | 95 | 27.0789 | 37.2 | 0 | 5 | 0
94 | 95 | 96 | 19.928 | 26 | 0 | 4 | 0
95 | 96 | 97 | 18.0951 | 26 | 0 | 3 | 0
96 | 97 | 98 | 17.3319 | 26 | 0 | 2 | 0
97 | 98 | 99 | 23.4142 | 20 | 0 | 1 | 0
98 | 90 | 100 | 30.8148 | 37.2 | 0 | 10 | 1 | 228 | 934
99 | 100 | 101 | 18.2439 | 37.2 | 0 | 9 | 0
100 | 101 | 102 | 17.3319 | 37.2 | 0 | 8 | 0
101 | 102 | 103 | 17.7853 | 37.2 | 0 | 7 | 0
102 | 103 | 104 | 16.7323 | 37.2 | 0 | 6 | 0
103 | 104 | 105 | 17.3319 | 37.2 | 0 | 5 | 0
104 | 105 | 106 | 17.4872 | 26 | 0 | 4 | 0
105 | 106 | 107 | 18.3178 | 26 | 0 | 3 | 0
106 | 107 | 108 | 17.4098 | 26 | 0 | 2 | 0
107 | 108 | 109 | 19.7615 | 20 | 0 | 1 | 0
108 | 58 | 110 | 51.7555 | 82.5 | 0 | 101 | 0
109 | 110 | 111 | 49.4037 | 54.5 | 0 | 32 | 1 | 631 | 358
110 | 111 | 112 | 33.3927 | 37.2 | 0 | 11 | 0
111 | 112 | 113 | 15.6947 | 37.2 | 0 | 10 | 0
112 | 113 | 114 | 25.7658 | 37.2 | 0 | 9 | 0
113 | 114 | 115 | 35.3716 | 37.2 | 0 | 8 | 1 | 747 | 191
114 | 115 | 116 | 45.82 | 37.2 | 0 | 7 | 0
115 | 116 | 117 | 22.691 | 37.2 | 0 | 6 | 0
116 | 117 | 118 | 20.2865 | 37.2 | 0 | 5 | 0
117 | 118 | 119 | 23.1302 | 26 | 0 | 4 | 0
118 | 119 | 120 | 18.7474 | 26 | 0 | 3 | 0
119 | 120 | 121 | 23.574 | 26 | 0 | 2 | 0
120 | 121 | 122 | 21.0567 | 20 | 0 | 1 | 0
121 | 111 | 123 | 34.4029 | 43.1 | 0 | 14 | 0
122 | 123 | 124 | 12.5103 | 37.2 | 0 | 13 | 0
123 | 124 | 125 | 10.8099 | 37.2 | 0 | 12 | 0
124 | 125 | 126 | 11.8569 | 37.2 | 0 | 11 | 0
125 | 126 | 127 | 11.2857 | 37.2 | 0 | 10 | 0
126 | 127 | 128 | 12.7481 | 37.2 | 0 | 9 | 0
127 | 128 | 129 | 7.0189 | 37.2 | 0 | 8 | 0
128 | 129 | 130 | 12.7834 | 37.2 | 0 | 7 | 0
129 | 130 | 131 | 8.3661 | 37.2 | 0 | 6 | 0
130 | 131 | 132 | 18.2439 | 37.2 | 0 | 5 | 0
131 | 132 | 133 | 8.8546 | 26 | 0 | 3 | 0
132 | 133 | 134 | 9.3335 | 26 | 0 | 2 | 0
133 | 134 | 135 | 14.7474 | 20 | 0 | 1 | 0
134 | 111 | 136 | 27.2613 | 37.2 | 0 | 7 | 0
135 | 136 | 137 | 24.8156 | 37.2 | 0 | 6 | 0
136 | 137 | 138 | 34.5988 | 37.2 | 0 | 5 | 1 | 591 | 506
137 | 138 | 139 | 28.2941 | 26 | 0 | 4 | 0
138 | 139 | 140 | 21.1492 | 26 | 0 | 3 | 0
139 | 140 | 141 | 21.1492 | 26 | 0 | 2 | 0
140 | 141 | 142 | 20.5221 | 20 | 0 | 1 | 0
141 | 110 | 143 | 15.4439 | 70.3 | 0 | 69 | 0
142 | 143 | 144 | 17.8948 | 37.2 | 0 | 6 | 0
143 | 144 | 145 | 25.0025 | 37.2 | 0 | 5 | 0
144 | 145 | 146 | 35.2994 | 26 | 0 | 4 | 0
145 | 146 | 147 | 22.7966 | 26 | 0 | 3 | 0
146 | 147 | 148 | 28.679 | 26 | 0 | 2 | 0
147 | 148 | 149 | 32.3556 | 20 | 0 | 1 | 0
148 | 143 | 150 | 24.7671 | 37.2 | 0 | 6 | 0
149 | 150 | 151 | 25.0025 | 37.2 | 0 | 5 | 0
150 | 151 | 152 | 24.0409 | 26 | 0 | 4 | 0
151 | 152 | 153 | 30.8927 | 26 | 0 | 3 | 0
152 | 153 | 154 | 23.5421 | 26 | 0 | 2 | 0
153 | 154 | 155 | 25.4962 | 20 | 0 | 1 | 0
154 | 143 | 156 | 23.777 | 70.3 | 0 | 57 | 0
155 | 156 | 157 | 17.6752 | 37.2 | 0 | 6 | 0
156 | 157 | 158 | 26.99 | 37.2 | 0 | 5 | 0
157 | 158 | 159 | 27.6986 | 26 | 0 | 4 | 0
158 | 159 | 160 | 25.7658 | 26 | 0 | 3 | 0
159 | 160 | 161 | 29.4133 | 26 | 0 | 2 | 0
160 | 161 | 162 | 29.1723 | 20 | 0 | 1 | 0
161 | 156 | 163 | 26.9622 | 37.2 | 0 | 6 | 0
162 | 163 | 164 | 23.1042 | 37.2 | 0 | 5 | 0
163 | 164 | 165 | 28.9241 | 26 | 0 | 4 | 0
164 | 165 | 166 | 26.99 | 26 | 0 | 3 | 0
165 | 166 | 167 | 21.8204 | 26 | 0 | 2 | 0
166 | 167 | 168 | 27.9469 | 20 | 0 | 1 | 0
167 | 156 | 169 | 31.6658 | 70.3 | 0 | 45 | 0
168 | 169 | 170 | 25.2476 | 37.2 | 0 | 5 | 0
169 | 170 | 171 | 23.2855 | 26 | 0 | 4 | 0
170 | 171 | 172 | 26.9622 | 26 | 0 | 3 | 0
171 | 172 | 173 | 29.4388 | 26 | 0 | 2 | 0
172 | 173 | 174 | 26.4731 | 20 | 0 | 1 | 0
173 | 169 | 175 | 27.7149 | 37.2 | 0 | 9 | 0
174 | 175 | 176 | 25.0025 | 26 | 0 | 4 | 0
175 | 176 | 177 | 22.3172 | 26 | 0 | 3 | 0
176 | 177 | 178 | 25.4962 | 26 | 0 | 2 | 0
177 | 178 | 179 | 20.8704 | 20 | 0 | 1 | 0
178 | 175 | 180 | 32.6145 | 37.2 | 0 | 5 | 0
179 | 180 | 181 | 26.228 | 26 | 0 | 3 | 0
180 | 181 | 182 | 26.4901 | 26 | 0 | 2 | 0
181 | 182 | 183 | 24.2709 | 20 | 0 | 1 | 0
182 | 180 | 184 | 37.9605 | 26 | 0 | 2 | 1 | 330 | 305
183 | 184 | 185 | 25.4962 | 20 | 0 | 1 | 0
184 | 169 | 186 | 52.2092 | 54.5 | 0 | 31 | 0
185 | 186 | 187 | 18.6349 | 26 | 0 | 4 | 0
186 | 187 | 188 | 21.592 | 26 | 0 | 2 | 0
187 | 186 | 189 | 28.2144 | 54.5 | 0 | 27 | 0
188 | 189 | 190 | 18.1531 | 26 | 0 | 3 | 0
189 | 190 | 191 | 26.9622 | 26 | 0 | 2 | 0
190 | 191 | 192 | 31.13 | 20 | 0 | 1 | 0
191 | 189 | 193 | 27.2117 | 54.5 | 0 | 24 | 0
192 | 193 | 194 | 19.6089 | 26 | 0 | 3 | 0
193 | 194 | 195 | 25.9921 | 26 | 0 | 2 | 0
194 | 195 | 196 | 29.1723 | 20 | 0 | 1 | 0
195 | 193 | 197 | 30.8684 | 43.1 | 0 | 21 | 0
196 | 197 | 198 | 15.6947 | 26 | 0 | 3 | 0
197 | 198 | 199 | 29.9397 | 26 | 0 | 2 | 0
198 | 199 | 200 | 29.6675 | 20 | 0 | 1 | 0
199 | 197 | 201 | 29.234 | 43.1 | 0 | 18 | 0
200 | 201 | 202 | 21.592 | 26 | 0 | 3 | 0
201 | 202 | 203 | 25.9921 | 26 | 0 | 2 | 0
202 | 203 | 204 | 26.99 | 20 | 0 | 1 | 0
203 | 201 | 205 | 36.3227 | 43.1 | 0 | 15 | 0
204 | 205 | 206 | 12.7481 | 26 | 0 | 3 | 0
205 | 206 | 207 | 24.2709 | 26 | 0 | 2 | 0
206 | 207 | 208 | 29.9397 | 20 | 0 | 1 | 0
207 | 205 | 209 | 13.5367 | 37.2 | 0 | 12 | 0
208 | 209 | 210 | 22.5515 | 26 | 0 | 3 | 0
209 | 210 | 211 | 28.679 | 26 | 0 | 2 | 0
210 | 211 | 212 | 23.0456 | 20 | 0 | 1 | 0
211 | 209 | 213 | 29.6625 | 37.2 | 0 | 9 | 0
212 | 213 | 214 | 23.0521 | 26 | 0 | 3 | 0
213 | 214 | 215 | 27.2172 | 26 | 0 | 2 | 0
214 | 215 | 216 | 25.0025 | 20 | 0 | 1 | 0
215 | 213 | 217 | 21.0852 | 26 | 0 | 2 | 0
216 | 217 | 218 | 25.5021 | 20 | 0 | 1 | 0
217 | 213 | 219 | 31.1445 | 26 | 0 | 4 | 0
218 | 219 | 220 | 17.7091 | 26 | 0 | 3 | 0
219 | 220 | 221 | 25.0205 | 26 | 0 | 2 | 0
220 | 221 | 222 | 24.5111 | 20 | 0 | 1 | 0

## EUList
End-User No | Node in Connection | kV | x Coordinate | y Coordinate | P_euS | P_euR
1 | 4 | 3 | 851 | 787 | 1.9937 | 1.7626
2 | 5 | 4 | 832 | 805 | 2.1224 | 1.9395
3 | 6 | 2 | 808 | 828 | 2.1 | 1.9831
4 | 7 | 3 | 790 | 847 | 2.1269 | 1.9893
5 | 8 | 5 | 767 | 866 | 2.1092 | 1.9771
6 | 9 | 5 | 750 | 885 | 2.0178 | 1.989
7 | 10 | 2 | 726 | 907 | 2.0189 | 1.9989
8 | 11 | 1 | 707 | 922 | 1.9942 | 1.9924
9 | 12 | 4 | 685 | 948 | 2.0082 | 1.9985
10 | 13 | 5 | 895 | 756 | 2.3637 | 1.6935
11 | 14 | 2 | 917 | 787 | 2.4244 | 1.901
12 | 16 | 4 | 881 | 826 | 2.0801 | 1.9615
13 | 16 | 3 | 911 | 860 | 2.0801 | 1.9785
14 | 17 | 4 | 863 | 847 | 1.9348 | 1.9155
15 | 17 | 1 | 890 | 878 | 2.0893 | 1.9155
16 | 18 | 3 | 841 | 866 | 2.0394 | 1.9941
17 | 18 | 5 | 868 | 900 | 2.0339 | 1.9726
18 | 19 | 4 | 816 | 886 | 1.9834 | 1.9809
19 | 19 | 4 | 848 | 917 | 2.0137 | 1.9943
20 | 20 | 5 | 784 | 914 | 1.9933 | 1.9913
21 | 20 | 2 | 813 | 949 | 2.0317 | 1.9977
22 | 21 | 1 | 767 | 935 | 2.0143 | 1.9973
23 | 21 | 2 | 796 | 965 | 2.0143 | 1.9973
24 | 22 | 1 | 737 | 961 | 2.0123 | 1.9985
25 | 22 | 1 | 767 | 993 | 1.999 | 1.9979
26 | 23 | 4 | 716 | 982 | 1.9989 | 1.9986
27 | 23 | 3 | 746 | 1014 | 2 | 1.9995
28 | 25 | 4 | 957 | 907 | 1.9835 | 1.9628
29 | 26 | 3 | 937 | 929 | 2.0089 | 1.9921
30 | 27 | 3 | 959 | 970 | 1.9902 | 1.9796
31 | 28 | 2 | 913 | 951 | 2.0752 | 1.9907
32 | 28 | 5 | 945 | 987 | 1.9885 | 1.9875
33 | 29 | 1 | 893 | 971 | 2.029 | 1.9993
34 | 30 | 1 | 911 | 1012 | 1.9956 | 1.995
35 | 31 | 5 | 863 | 998 | 2.0276 | 1.9989
36 | 31 | 3 | 893 | 1032 | 2.0026 | 1.9998
37 | 32 | 2 | 848 | 1017 | 2.0016 | 1.9992
38 | 33 | 5 | 865 | 1059 | 2.0007 | 1.9996
39 | 34 | 5 | 822 | 1037 | 2.0062 | 2
40 | 35 | 5 | 845 | 1081 | 2.0003 | 2
41 | 36 | 2 | 800 | 1054 | 2.002 | 1.9999
42 | 37 | 2 | 988 | 1011 | 2 | 1.982
43 | 38 | 5 | 971 | 1029 | 2.0474 | 1.9904
44 | 39 | 1 | 943 | 1053 | 1.9972 | 1.9936
45 | 40 | 3 | 924 | 1068 | 2.0508 | 1.9979
46 | 41 | 3 | 897 | 1096 | 1.9984 | 1.9966
47 | 42 | 3 | 883 | 1114 | 2.0021 | 1.9985
48 | 44 | 2 | 769 | 715 | 1.9829 | 1.8483
49 | 45 | 1 | 749 | 733 | 1.9323 | 1.8497
50 | 46 | 1 | 729 | 754 | 1.9536 | 1.8965
51 | 47 | 4 | 711 | 769 | 1.9683 | 1.9796
52 | 48 | 1 | 688 | 787 | 1.9683 | 1.9346
53 | 49 | 2 | 670 | 809 | 1.9681 | 1.9586
54 | 50 | 5 | 645 | 829 | 1.989 | 1.9918
55 | 51 | 3 | 626 | 844 | 1.989 | 1.9773
56 | 53 | 1 | 750 | 681 | 2.1219 | 1.8101
57 | 54 | 1 | 728 | 702 | 2.1219 | 1.9183
58 | 55 | 4 | 717 | 717 | 2.0841 | 1.9444
59 | 56 | 2 | 637 | 787 | 1.9625 | 1.957
60 | 57 | 5 | 619 | 805 | 2.0124 | 1.9972
61 | 60 | 4 | 355 | 738 | 2.0649 | 1.9468
62 | 61 | 3 | 343 | 711 | 1.9574 | 1.9448
63 | 62 | 4 | 327 | 682 | 1.9576 | 1.9538
64 | 63 | 2 | 313 | 655 | 2.1424 | 1.9896
65 | 64 | 5 | 295 | 624 | 2.1424 | 1.9975
66 | 65 | 4 | 280 | 593 | 2.007 | 1.9935
67 | 66 | 3 | 262 | 563 | 2.0009 | 1.9995
68 | 68 | 1 | 417 | 790 | 2.0396 | 1.9819
69 | 69 | 4 | 433 | 811 | 2.1502 | 1.9951
70 | 69 | 1 | 397 | 837 | 2.0329 | 1.9691
71 | 70 | 2 | 459 | 847 | 1.9895 | 1.9863
72 | 70 | 5 | 424 | 873 | 2.0129 | 1.9898
73 | 71 | 2 | 479 | 874 | 2.0932 | 1.9984
74 | 71 | 2 | 446 | 897 | 2.0016 | 1.9972
75 | 72 | 3 | 497 | 897 | 1.9981 | 1.997
76 | 72 | 1 | 463 | 923 | 1.9981 | 1.997
77 | 73 | 1 | 515 | 918 | 2.0031 | 1.9995
78 | 73 | 3 | 476 | 947 | 1.9996 | 1.9991
79 | 74 | 4 | 533 | 942 | 2.0098 | 2
80 | 74 | 1 | 492 | 969 | 1.9997 | 1.9996
81 | 76 | 5 | 320 | 878 | 1.9999 | 1.9773
82 | 77 | 1 | 329 | 916 | 2.0091 | 1.9946
83 | 78 | 1 | 341 | 954 | 2.0028 | 1.9996
84 | 79 | 4 | 353 | 995 | 1.9972 | 1.997
85 | 80 | 2 | 365 | 1035 | 2.0005 | 2
86 | 81 | 2 | 288 | 821 | 2.0005 | 1.9951
87 | 82 | 3 | 272 | 794 | 2.0005 | 1.9989
88 | 83 | 5 | 253 | 768 | 2.002 | 1.9987
89 | 84 | 5 | 232 | 738 | 2.0024 | 1.9992
90 | 85 | 5 | 216 | 710 | 2.0035 | 1.9995
91 | 86 | 4 | 195 | 678 | 2.0146 | 2
92 | 87 | 4 | 174 | 646 | 1.9996 | 1.9995
93 | 88 | 2 | 158 | 623 | 1.9998 | 1.9997
94 | 89 | 1 | 141 | 598 | 2.0005 | 2
95 | 91 | 4 | 255 | 856 | 2.1395 | 1.9976
96 | 92 | 4 | 232 | 825 | 2.0095 | 1.9995
97 | 93 | 2 | 210 | 791 | 2 | 1.9987
98 | 94 | 2 | 191 | 761 | 2.0013 | 1.9999
99 | 95 | 5 | 163 | 723 | 1.9988 | 1.9984
100 | 96 | 2 | 143 | 693 | 2.001 | 2
101 | 97 | 2 | 125 | 663 | 1.9997 | 1.9996
102 | 98 | 4 | 106 | 637 | 1.9998 | 1.9997
103 | 99 | 5 | 83 | 598 | 2.0002 | 1.9998
104 | 100 | 3 | 219 | 885 | 2.0056 | 1.9979
105 | 101 | 4 | 199 | 855 | 1.9961 | 1.9949
106 | 102 | 2 | 183 | 831 | 2.0129 | 1.9998
107 | 103 | 3 | 163 | 804 | 1.9984 | 1.998
108 | 104 | 1 | 147 | 778 | 2.0044 | 1.9998
109 | 105 | 4 | 129 | 751 | 2.0004 | 1.9998
110 | 106 | 2 | 110 | 726 | 2.0028 | 1.9998
111 | 107 | 3 | 93 | 698 | 2 | 1.9999
112 | 108 | 3 | 76 | 672 | 2.0002 | 2
113 | 109 | 4 | 56 | 641 | 2 | 2
114 | 112 | 2 | 716 | 333 | 2.0122 | 1.9889
115 | 113 | 5 | 725 | 303 | 1.9772 | 1.9739
116 | 114 | 5 | 739 | 261 | 2.0574 | 1.9956
117 | 115 | 5 | 756 | 228 | 1.9915 | 1.9907
118 | 116 | 4 | 822 | 282 | 2.0163 | 1.9997
119 | 117 | 4 | 859 | 303 | 1.9976 | 1.9974
120 | 118 | 4 | 889 | 323 | 2.0018 | 1.9999
121 | 119 | 5 | 921 | 348 | 2.0009 | 2
122 | 120 | 1 | 951 | 371 | 2.0002 | 1.9999
123 | 121 | 5 | 983 | 395 | 2.0014 | 2
124 | 122 | 1 | 1017 | 418 | 2.0001 | 2
125 | 123 | 5 | 740 | 384 | 2.0333 | 1.9788
126 | 124 | 1 | 726 | 441 | 1.9993 | 1.988
127 | 125 | 2 | 770 | 412 | 1.9993 | 1.9958
128 | 126 | 3 | 761 | 462 | 1.9999 | 1.9958
129 | 127 | 1 | 808 | 432 | 2 | 1.9975
130 | 128 | 3 | 796 | 485 | 2.0476 | 1.9993
131 | 129 | 4 | 839 | 450 | 1.9981 | 1.9975
132 | 130 | 2 | 830 | 505 | 2.0015 | 1.9999
133 | 131 | 2 | 871 | 470 | 2.0036 | 1.9998
134 | 132 | 5 | 897 | 491 | 1.9997 | 1.9996
135 | 132 | 4 | 871 | 528 | 2 | 1.9998
136 | 133 | 2 | 900 | 542 | 2.001 | 2
137 | 134 | 5 | 929 | 520 | 2.0023 | 1.9999
138 | 135 | 5 | 951 | 497 | 2.0011 | 2
139 | 136 | 2 | 663 | 435 | 1.9765 | 1.9635
140 | 137 | 1 | 640 | 469 | 2.1164 | 1.9747
141 | 138 | 3 | 630 | 504 | 2.1164 | 1.9824
142 | 139 | 4 | 672 | 532 | 2.1164 | 1.9993
143 | 140 | 2 | 703 | 552 | 2.0092 | 1.9994
144 | 141 | 4 | 737 | 575 | 1.9985 | 1.9982
145 | 142 | 3 | 769 | 593 | 2.0003 | 2
146 | 144 | 1 | 562 | 375 | 2.0003 | 1.9716
147 | 145 | 2 | 584 | 335 | 1.9777 | 1.9499
148 | 146 | 4 | 612 | 281 | 2.006 | 1.995
149 | 147 | 4 | 633 | 239 | 1.9964 | 1.9944
150 | 148 | 4 | 655 | 194 | 2.0019 | 1.9998
151 | 149 | 3 | 681 | 142 | 2.0027 | 2
152 | 150 | 5 | 527 | 449 | 1.9967 | 1.9624
153 | 151 | 2 | 511 | 491 | 1.9967 | 1.992
154 | 152 | 4 | 492 | 528 | 2.0043 | 1.9912
155 | 153 | 1 | 468 | 579 | 2.0864 | 1.9996
156 | 154 | 4 | 451 | 615 | 2.031 | 1.9995
157 | 155 | 3 | 430 | 662 | 2.0004 | 2
158 | 157 | 2 | 520 | 358 | 1.9994 | 1.9524
159 | 158 | 4 | 544 | 313 | 1.9994 | 1.9863
160 | 159 | 3 | 565 | 270 | 2.035 | 1.993
161 | 160 | 3 | 587 | 228 | 2.0014 | 1.9976
162 | 161 | 1 | 611 | 176 | 2.002 | 1.9999
163 | 162 | 5 | 632 | 132 | 2.0004 | 1.9999
164 | 163 | 2 | 487 | 430 | 2.0004 | 1.9919
165 | 164 | 4 | 470 | 469 | 2.0532 | 1.989
166 | 165 | 1 | 448 | 517 | 2.0139 | 1.989
167 | 166 | 5 | 427 | 559 | 1.9941 | 1.9923
168 | 167 | 1 | 411 | 597 | 1.9986 | 1.9967
169 | 168 | 1 | 390 | 644 | 2.0009 | 1.9998
170 | 170 | 2 | 434 | 404 | 2.0724 | 1.9846
171 | 171 | 2 | 415 | 444 | 2.017 | 1.9896
172 | 172 | 3 | 395 | 488 | 1.9889 | 1.9879
173 | 173 | 4 | 372 | 535 | 1.9977 | 1.9946
174 | 174 | 1 | 351 | 579 | 1.9953 | 1.9946
175 | 176 | 2 | 391 | 383 | 2.009 | 1.9981
176 | 177 | 3 | 373 | 419 | 2.0098 | 1.9909
177 | 178 | 5 | 355 | 465 | 2.0068 | 1.9937
178 | 179 | 1 | 339 | 497 | 2.0201 | 1.9976
179 | 181 | 1 | 338 | 361 | 2.136 | 1.9941
180 | 182 | 1 | 317 | 405 | 1.9962 | 1.992
181 | 183 | 4 | 298 | 447 | 2.0018 | 1.9994
182 | 184 | 2 | 290 | 338 | 1.9924 | 1.9881
183 | 185 | 3 | 271 | 379 | 1.9895 | 1.9879
184 | 187 | 3 | 498 | 255 | 2.0092 | 1.999
185 | 187 | 4 | 479 | 288 | 2.0969 | 1.9959
186 | 188 | 2 | 463 | 237 | 2.0465 | 1.9993
187 | 188 | 3 | 445 | 270 | 2.0012 | 1.9993
188 | 190 | 1 | 532 | 199 | 2.0032 | 1.9937
189 | 191 | 3 | 558 | 156 | 2.0016 | 1.9971
190 | 192 | 3 | 582 | 103 | 2.0015 | 1.9999
191 | 194 | 5 | 490 | 177 | 2.0028 | 1.9945
192 | 195 | 5 | 513 | 134 | 1.9927 | 1.9921
193 | 196 | 4 | 535 | 84 | 2 | 1.9988
194 | 198 | 1 | 432 | 163 | 2.006 | 1.9994
195 | 199 | 3 | 454 | 119 | 1.9986 | 1.9978
196 | 200 | 1 | 478 | 68 | 1.9994 | 1.9991
197 | 202 | 5 | 384 | 151 | 2.0046 | 1.9957
198 | 203 | 5 | 405 | 106 | 2.0072 | 1.9996
199 | 204 | 3 | 425 | 62 | 1.9989 | 1.9986
200 | 206 | 4 | 310 | 158 | 1.997 | 1.9967
201 | 207 | 2 | 330 | 120 | 2.0024 | 1.9978
202 | 208 | 1 | 353 | 67 | 2.0002 | 1.9999
203 | 210 | 3 | 270 | 238 | 2.0019 | 1.9983
204 | 211 | 3 | 247 | 285 | 2.0008 | 1.9995
205 | 212 | 4 | 231 | 323 | 2.0004 | 2
206 | 214 | 2 | 260 | 138 | 1.9998 | 1.9996
207 | 215 | 3 | 281 | 93 | 2.002 | 1.9998
208 | 216 | 5 | 305 | 57 | 2.0003 | 2
209 | 217 | 5 | 227 | 209 | 1.9998 | 1.9994
210 | 218 | 1 | 205 | 253 | 2.0003 | 2.0002
211 | 219 | 4 | 187 | 147 | 2.0002 | 2
212 | 220 | 3 | 207 | 120 | 1.9999 | 1.9998
213 | 221 | 3 | 228 | 81 | 2 | 1.9999
214 | 222 | 3 | 249 | 37 | 2 | 2

## NodeList
Node No | x Coordinate | y Coordinate | P_nodeS | P_nodeR
1 | 1045 | 536 | 3.0067 | 1
2 | 838 | 726 | 2.6233 | 1.3834
3 | 858 | 750 | 2.546 | 1.4606
4 | 838 | 770 | 2.3346 | 1.6721
5 | 818 | 791 | 2.1911 | 1.8156
6 | 793 | 812 | 2.1055 | 1.9011
7 | 777 | 831 | 2.0736 | 1.9331
8 | 752 | 853 | 2.0555 | 1.9512
9 | 736 | 869 | 2.0313 | 1.9754
10 | 712 | 891 | 2.0177 | 1.989
11 | 695 | 908 | 2.0154 | 1.9913
12 | 671 | 931 | 2.0107 | 1.9959
13 | 875 | 772 | 2.4182 | 1.5792
14 | 900 | 800 | 2.2893 | 1.7081
15 | 918 | 821 | 2.2209 | 1.7765
16 | 894 | 843 | 2.1191 | 1.8784
17 | 877 | 860 | 2.0915 | 1.9059
18 | 853 | 883 | 2.0378 | 1.9596
19 | 831 | 903 | 2.0191 | 1.9783
20 | 800 | 932 | 2.0075 | 1.99
21 | 781 | 951 | 2.0043 | 1.9931
22 | 753 | 978 | 1.9999 | 1.9975
23 | 732 | 997 | 1.999 | 1.9984
24 | 989 | 912 | 2.0693 | 1.9326
25 | 973 | 926 | 2.0561 | 1.9458
26 | 953 | 946 | 2.0308 | 1.9711
27 | 945 | 954 | 2.025 | 1.9769
28 | 929 | 968 | 2.0163 | 1.9857
29 | 907 | 988 | 2.0094 | 1.9925
30 | 898 | 997 | 2.0078 | 1.9941
31 | 878 | 1016 | 2.005 | 1.9969
32 | 861 | 1031 | 2.0043 | 1.9977
33 | 850 | 1042 | 2.0031 | 1.9989
34 | 838 | 1054 | 2.0024 | 1.9995
35 | 830 | 1062 | 2.0023 | 1.9997
36 | 816 | 1073 | 2.0021 | 1.9998
37 | 1004 | 1029 | 2.0275 | 1.9731
38 | 987 | 1049 | 2.0223 | 1.9782
39 | 961 | 1070 | 2.0106 | 1.9899
40 | 941 | 1091 | 2.006 | 1.9945
41 | 916 | 1114 | 2.0045 | 1.996
42 | 899 | 1131 | 2.0031 | 1.9974
43 | 815 | 701 | 2.0031 | 1.4275
44 | 782 | 731 | 2.2592 | 1.7072
45 | 764 | 747 | 2.1763 | 1.7901
46 | 741 | 767 | 2.1124 | 1.8539
47 | 724 | 784 | 2.0828 | 1.8835
48 | 703 | 803 | 2.0393 | 1.927
49 | 682 | 822 | 2.0128 | 1.9535
50 | 660 | 842 | 1.9963 | 1.9701
51 | 641 | 859 | 1.992 | 1.9743
52 | 761 | 642 | 1.992 | 1.5054
53 | 735 | 664 | 1.992 | 1.6368
54 | 714 | 686 | 2.1718 | 1.8379
55 | 699 | 698 | 2.1223 | 1.8874
56 | 622 | 772 | 2.058 | 1.9517
57 | 603 | 788 | 2.0317 | 1.9779
58 | 553 | 514 | 2.0317 | 1.6892
59 | 401 | 767 | 2.1176 | 1.8827
60 | 376 | 727 | 2.077 | 1.9234
61 | 363 | 698 | 2.0622 | 1.9382
62 | 347 | 671 | 2.0522 | 1.9482
63 | 333 | 645 | 2.0239 | 1.9765
64 | 317 | 613 | 2.011 | 1.9894
65 | 298 | 582 | 2.0079 | 1.9925
66 | 282 | 551 | 2.0033 | 1.9971
67 | 385 | 785 | 2.1171 | 1.8927
68 | 398 | 806 | 2.0709 | 1.9389
69 | 414 | 825 | 2.0446 | 1.9651
70 | 439 | 862 | 2.0254 | 1.9844
71 | 462 | 889 | 2.0169 | 1.9928
72 | 479 | 912 | 2.0147 | 1.9951
73 | 495 | 933 | 2.0114 | 1.9984
74 | 512 | 957 | 2.0105 | 1.9992
75 | 292 | 866 | 2.0385 | 1.962
76 | 298 | 883 | 2.0342 | 1.9663
77 | 309 | 922 | 2.0133 | 1.9872
78 | 320 | 961 | 2.0056 | 1.9949
79 | 331 | 998 | 2.0041 | 1.9964
80 | 343 | 1040 | 2.0016 | 1.9989
81 | 271 | 833 | 2.0195 | 1.981
82 | 252 | 807 | 2.0111 | 1.9894
83 | 236 | 778 | 2.0068 | 1.9937
84 | 216 | 750 | 2.0045 | 1.996
85 | 198 | 720 | 2.0035 | 1.997
86 | 177 | 690 | 2.0016 | 1.9989
87 | 157 | 657 | 2.0011 | 1.9994
88 | 140 | 632 | 2.0009 | 1.9996
89 | 125 | 611 | 2.0007 | 1.9998
90 | 258 | 901 | 2.0198 | 1.9803
91 | 236 | 868 | 2.0105 | 1.9896
92 | 214 | 837 | 2.0058 | 1.9942
93 | 192 | 803 | 2.0035 | 1.9965
94 | 174 | 773 | 2.0025 | 1.9976
95 | 145 | 733 | 2.002 | 1.9981
96 | 126 | 702 | 2.0008 | 1.9993
97 | 107 | 675 | 2.0005 | 1.9995
98 | 89 | 649 | 2.0004 | 1.9996
99 | 66 | 613 | 2.0003 | 1.9997
100 | 202 | 896 | 2.0091 | 1.9909
101 | 184 | 868 | 2.0059 | 1.9941
102 | 166 | 842 | 2.0036 | 1.9965
103 | 148 | 815 | 2.0024 | 1.9976
104 | 132 | 789 | 2.0016 | 1.9984
105 | 114 | 763 | 2.0012 | 1.9988
106 | 97 | 736 | 2.0005 | 1.9995
107 | 76 | 710 | 2.0002 | 1.9998
108 | 61 | 682 | 2.0001 | 1.9999
109 | 41 | 652 | 2 | 2
110 | 592 | 428 | 2.1775 | 1.8226
111 | 667 | 378 | 2.0847 | 1.9155
112 | 691 | 322 | 2.0396 | 1.9606
113 | 703 | 296 | 2.0297 | 1.9705
114 | 722 | 253 | 2.0177 | 1.9825
115 | 771 | 211 | 2.0108 | 1.9893
116 | 838 | 261 | 2.0045 | 1.9956
117 | 871 | 286 | 2.0032 | 1.997
118 | 900 | 309 | 2.0023 | 1.9978
119 | 934 | 334 | 2.0008 | 1.9994
120 | 961 | 355 | 2.0003 | 1.9998
121 | 996 | 380 | 2.0002 | 1.9999
122 | 1026 | 404 | 2.0002 | 2
123 | 721 | 410 | 2.0465 | 1.9546
124 | 741 | 421 | 2.0278 | 1.9733
125 | 758 | 431 | 2.0177 | 1.9834
126 | 776 | 443 | 2.0114 | 1.9898
127 | 794 | 453 | 2.0076 | 1.9935
128 | 815 | 463 | 2.005 | 1.9962
129 | 825 | 471 | 2.0041 | 1.997
130 | 845 | 483 | 2.0029 | 1.9982
131 | 858 | 491 | 2.0024 | 1.9987
132 | 886 | 509 | 2.0019 | 1.9992
133 | 901 | 515 | 2.0015 | 1.9996
134 | 914 | 504 | 2.0014 | 1.9998
135 | 932 | 484 | 2.0012 | 1.9999
136 | 642 | 421 | 2.0536 | 1.9468
137 | 619 | 460 | 2.0378 | 1.9626
138 | 615 | 523 | 2.0267 | 1.9736
139 | 659 | 550 | 2.0077 | 1.9926
140 | 692 | 570 | 2.0035 | 1.9969
141 | 725 | 590 | 2.0025 | 1.9979
142 | 756 | 611 | 2.001 | 1.9993
143 | 567 | 415 | 2.1328 | 1.8699
144 | 582 | 386 | 2.0947 | 1.908
145 | 602 | 345 | 2.075 | 1.9277
146 | 630 | 287 | 2.0221 | 1.9806
147 | 649 | 250 | 2.0116 | 1.9911
148 | 672 | 203 | 2.0063 | 1.9964
149 | 698 | 150 | 2.0036 | 1.9991
150 | 548 | 456 | 2.0783 | 1.9221
151 | 528 | 497 | 2.0529 | 1.9475
152 | 510 | 537 | 2.0205 | 1.9799
153 | 486 | 588 | 2.006 | 1.9944
154 | 468 | 627 | 2.0029 | 1.9974
155 | 448 | 669 | 2.0011 | 1.9993
156 | 528 | 396 | 2.0948 | 1.9055
157 | 544 | 368 | 2.0692 | 1.9311
158 | 564 | 323 | 2.0477 | 1.9526
159 | 587 | 278 | 2.0166 | 1.9837
160 | 606 | 235 | 2.0064 | 1.9939
161 | 630 | 187 | 2.0027 | 1.9976
162 | 653 | 139 | 2.001 | 1.9993
163 | 506 | 440 | 2.0535 | 1.9471
164 | 490 | 479 | 2.0398 | 1.9608
165 | 466 | 526 | 2.0175 | 1.9832
166 | 446 | 571 | 2.0095 | 1.9911
167 | 429 | 607 | 2.006 | 1.9947
168 | 407 | 653 | 2.0023 | 1.9984
169 | 475 | 373 | 2.0651 | 1.9248
170 | 454 | 414 | 2.0426 | 1.9473
171 | 435 | 452 | 2.0134 | 1.9765
172 | 413 | 496 | 2.0038 | 1.9862
173 | 391 | 545 | 1.9985 | 1.9914
174 | 369 | 588 | 1.9962 | 1.9937
175 | 429 | 352 | 2.0617 | 1.9559
176 | 409 | 393 | 2.0338 | 1.9839
177 | 392 | 430 | 2.0281 | 1.9896
178 | 372 | 472 | 2.025 | 1.9927
179 | 357 | 507 | 2.0217 | 1.996
180 | 375 | 327 | 2.0331 | 1.9682
181 | 354 | 370 | 2.0151 | 1.9861
182 | 334 | 414 | 2.0105 | 1.9908
183 | 315 | 454 | 2.0044 | 1.9969
184 | 309 | 348 | 1.9957 | 1.9818
185 | 289 | 390 | 1.9912 | 1.9862
186 | 518 | 288 | 2.087 | 1.9587
187 | 488 | 272 | 2.0558 | 1.99
188 | 452 | 256 | 2.0495 | 1.9963
189 | 539 | 241 | 2.0325 | 1.9689
190 | 555 | 212 | 2.0163 | 1.9852
191 | 577 | 168 | 2.0087 | 1.9928
192 | 602 | 117 | 2.0032 | 1.9982
193 | 495 | 218 | 2.0243 | 1.9746
194 | 511 | 186 | 2.012 | 1.9869
195 | 531 | 143 | 2.008 | 1.9909
196 | 554 | 95 | 2.0021 | 1.9968
197 | 441 | 202 | 2.0125 | 1.986
198 | 453 | 176 | 2.0053 | 1.9933
199 | 475 | 126 | 2.0022 | 1.9963
200 | 498 | 77 | 2.0001 | 1.9984
201 | 388 | 196 | 2.0062 | 1.9913
202 | 404 | 160 | 2.0024 | 1.995
203 | 424 | 117 | 2 | 1.9975
204 | 444 | 72 | 1.9992 | 1.9983
205 | 322 | 190 | 2.0053 | 1.9949
206 | 332 | 169 | 2.004 | 1.9962
207 | 351 | 129 | 2.0028 | 1.9974
208 | 373 | 79 | 2.0009 | 1.9993
209 | 309 | 211 | 2.004 | 1.9964
210 | 291 | 248 | 2.0024 | 1.998
211 | 268 | 295 | 2.0014 | 1.999
212 | 250 | 333 | 2.0007 | 1.9997
213 | 261 | 186 | 2.0022 | 1.9981
214 | 281 | 149 | 2.0011 | 1.9992
215 | 302 | 104 | 2.0007 | 1.9996
216 | 322 | 63 | 2.0004 | 1.9999
217 | 243 | 220 | 2.0015 | 1.9989
218 | 221 | 261 | 2.0007 | 1.9998
219 | 211 | 159 | 2.0006 | 1.9995
220 | 223 | 129 | 2.0003 | 1.9997
221 | 245 | 89 | 2.0002 | 1.9998
222 | 265 | 49 | 2.0001 | 2

## Result
Newton-Raphson
20.4232
6.411
2.092
1.6958
1.2259
0.85033
0.54459
0.34494
0.20512
0.088563
0.054136
4.319
3.8693
3.2732
1.9828
1.1856
0.95655
0.58676
0.37944
0.24107
0.097905
0.047387
1.2904
0.86304
0.7049
0.52696
0.47059
0.34647
0.25185
0.22369
0.11905
0.078782
0.05144
0.029906
0.012578
0.42733
0.3169
0.18574
0.1192
0.056009
0.03283
14.0121
1.9132
1.4092
1.0935
0.831
0.42159
0.32085
0.24062
0.059468
12.099
1.4939
0.93109
0.55931
0.25123
0.16942
10.6051
3.2519
0.69119
0.50241
0.40979
0.32503
0.18856
0.083998
0.052133
2.5607
1.0316
0.76773
0.48199
0.35241
0.19487
0.10333
0.044574
1.529
0.35415
0.2303
0.13118
0.054212
0.032357
0.5125
0.36995
0.25566
0.17675
0.11472
0.062035
0.02883
0.019946
0.012904
0.66239
0.34992
0.24645
0.16414
0.11447
0.063403
0.047501
0.020954
0.012941
0.0057087
0.31247
0.21644
0.18826
0.12533
0.10745
0.070009
0.037934
0.02273
0.013807
0.0034966
7.3532
2.0909
0.63872
0.42906
0.36525
0.22868
0.1905
0.11977
0.099599
0.051325
0.026942
0.013357
0.0031153
0.86502
0.67277
0.52696
0.39433
0.30618
0.237
0.17659
0.15661
0.11379
0.080122
0.040182
0.02276
0.0092336
0.5872
0.43056
0.29975
0.19056
0.096567
0.042339
0.025544
5.2623
0.80896
0.48186
0.29854
0.15445
0.092071
0.028635
0.80493
0.5504
0.28151
0.15586
0.074922
0.026181
3.6484
0.66367
0.48492
0.25405
0.14145
0.074176
0.023291
0.68521
0.41535
0.20647
0.11986
0.085182
0.037365
2.2995
0.51431
0.27019
0.13382
0.090322
0.029117
0.58001
0.25358
0.1104
0.072698
0.041207
0.32643
0.19268
0.089227
0.05381
0.13375
0.043416
1.2052
0.3176
0.11932
0.8876
0.22408
0.11692
0.043485
0.66351
0.18335
0.082812
0.047566
0.48016
0.15448
0.065186
0.025653
0.32568
0.088923
0.063023
0.015118
0.23676
0.065696
0.043024
0.024283
0.17106
0.05238
0.035898
0.015854
0.11868
0.041027
0.022852
0.0098643
0.037561
0.016944
0.040092
0.019674
0.013125
0.0048986
0.39618
0.46989
0.37559
0.30574
0.19965
0.13982
0.11656
0.034427
0.054136
0.44972
0.59613
0.37842
0.41883
0.11451
0.11451
0.23384
0.13595
0.054562
0.15276
0.036962
0.10141
0.071582
0.071582
0.032257
0.01826
0.014535
0.032852
0.15814
0.17794
0.05637
0.079836
0.044286
0.094621
0.028158
0.046522
0.058123
0.040266
0.027342
0.021534
0.017328
0.012578
0.11043
0.13117
0.066538
0.063191
0.023179
0.03283
0.50391
0.31578
0.26247
0.4094
0.10075
0.080225
0.18115
0.059468
0.5628
0.37178
0.30808
0.08181
0.16942
0.18878
0.092615
0.084759
0.13647
0.10456
0.031864
0.052133
0.26392
0.21634
0.069398
0.04621
0.083374
0.084566
0.072975
0.045765
0.045765
0.033077
0.025684
0.027148
0.017427
0.12385
0.09912
0.076965
0.021855
0.032357
0.14255
0.11429
0.078916
0.062027
0.052683
0.033205
0.0088842
0.0070416
0.012904
0.10347
0.082313
0.049669
0.051068
0.015903
0.026546
0.0080135
0.0072321
0.0057087
0.09603
0.028183
0.062931
0.017878
0.037441
0.032075
0.015204
0.0089223
0.010311
0.0034966
0.20966
0.063805
0.13657
0.038184
0.070726
0.020172
0.048274
0.024383
0.013585
0.010242
0.0031153
0.19225
0.14581
0.13263
0.088149
0.06918
0.06041
0.019984
0.04282
0.033664
0.017553
0.022387
0.017422
0.013526
0.0092336
0.15664
0.13081
0.1092
0.093987
0.054228
0.016796
0.025544
0.3271
0.18332
0.14409
0.062381
0.063436
0.028635
0.25453
0.26889
0.12565
0.08094
0.048741
0.026181
0.17874
0.23087
0.1126
0.067277
0.050884
0.023291
0.26986
0.20889
0.086605
0.034681
0.047818
0.037365
0.24412
0.13637
0.0435
0.061206
0.029117
0.14318
0.037703
0.031491
0.041207
0.10345
0.035417
0.05381
0.090334
0.043416
0.11097
0.08731
0.05966
0.05966
0.10717
0.07343
0.043485
0.10054
0.035246
0.047566
0.089297
0.039533
0.025653
0.025899
0.047906
0.015118
0.022672
0.018741
0.024283
0.016482
0.020044
0.015854
0.018175
0.012988
0.0098643
0.020617
0.016944
0.020418
0.0065488
0.0082261
0.0048986
6.411
2.092
1.6958
1.2259
0.85033
0.54459
0.34494
0.20512
0.088563
0.054136
4.319
3.8693
3.2732
1.9828
1.1856
0.95655
0.58676
0.37944
0.24107
0.097905
0.047387
1.2904
0.86304
0.7049
0.52696
0.47059
0.34647
0.25185
0.22369
0.11905
0.078782
0.05144
0.029906
0.012578
0.42733
0.3169
0.18574
0.1192
0.056009
0.03283
14.0121
1.9132
1.4092
1.0935
0.831
0.42159
0.32085
0.24062
0.059468
12.099
1.4939
0.93109
0.55931
0.25123
0.16942
10.6051
3.2519
0.69119
0.50241
0.40979
0.32503
0.18856
0.083998
0.052133
2.5607
1.0316
0.76773
0.48199
0.35241
0.19487
0.10333
0.044574
1.529
0.35415
0.2303
0.13118
0.054212
0.032357
0.5125
0.36995
0.25566
0.17675
0.11472
0.062035
0.02883
0.019946
0.012904
0.66239
0.34992
0.24645
0.16414
0.11447
0.063403
0.047501
0.020954
0.012941
0.0057087
0.31247
0.21644
0.18826
0.12533
0.10745
0.070009
0.037934
0.02273
0.013807
0.0034966
7.3532
2.0909
0.63872
0.42906
0.36525
0.22868
0.1905
0.11977
0.099599
0.051325
0.026942
0.013357
0.0031153
0.86502
0.67277
0.52696
0.39433
0.30618
0.237
0.17659
0.15661
0.11379
0.080122
0.040182
0.02276
0.0092336
0.5872
0.43056
0.29975
0.19056
0.096567
0.042339
0.025544
5.2623
0.80896
0.48186
0.29854
0.15445
0.092071
0.028635
0.80493
0.5504
0.28151
0.15586
0.074922
0.026181
3.6484
0.66367
0.48492
0.25405
0.14145
0.074176
0.023291
0.68521
0.41535
0.20647
0.11986
0.085182
0.037365
2.2995
0.51431
0.27019
0.13382
0.090322
0.029117
0.58001
0.25358
0.1104
0.072698
0.041207
0.32643
0.19268
0.089227
0.05381
0.13375
0.043416
1.2052
0.3176
0.11932
0.8876
0.22408
0.11692
0.043485
0.66351
0.18335
0.082812
0.047566
0.48016
0.15448
0.065186
0.025653
0.32568
0.088923
0.063023
0.015118
0.23676
0.065696
0.043024
0.024283
0.17106
0.05238
0.035898
0.015854
0.11868
0.041027
0.022852
0.0098643
0.037561
0.016944
0.040092
0.019674
0.013125
0.0048986